## Sheet1
Chamber 1
General Specification |  |  |  |  | Condition | Temperature (oC) | Humidity (%)
Product | Potato |  |  |  | Ambient | 30 | 70
Sack Dimension (2a,2b,L) ( in cm) | 47 | 32 | 94 |  | Inside Storage | 4 | 90
Weight of potato per sack (kg) | 50
Volume of potato per sack (cm3) | 111036.4507
No. of sacks(single layer) | 50
Number of layers of sacks in each pallet | 6
No. of sacks | 300
Capacity of cold store (MT) | 15
Volume of each pallet (m3) | 6.786
Room dimension (L,B,H) (in m) | 14.0208 | 4.2367 | 3.048
Total Volume of room (m3) | 181.0579
Store room dimension (L,B,H)(ft) | 39.234 | 10.234 | 8.2
Storage Volume(ft3) | 3292.4702
Transmission Load
Wall | Polyurethane Insulation Panel
Product Load
U- Value (W/m2.K) (Wall 80mm) | 0.275 |  |  |  | Specific Heat Capacity of potato (KJ/Kg.oC) | 3.39
U- Value (W/m2.K) (Floor 50mm) | 0.43 |  |  |  | Respiration heat (KJ/Kg per day) | 3.6
[5 empty] | Mass of potato (kg) | 15000
[5 empty] | Time taken to cool the product (days) | 7
Surface | Area (m2) | Temperature (oC) | Cooling Load (KWh/day) |  | Product exchange load (KWh/day) | 52.4643
North Wall | 42.7354 | 30 | 7.3334 |  | Product respiration load (KWh/day) | 15
West Wall | 12.9135 | 30 | 2.216 |  | Total Product Load (KWh/day) | 67.4643
East Wall | 12.9135 | 33 | 2.4716
South Wall | 42.7354 | 31 | 7.6154
Ceiling | 59.4022 | 41 | 14.506
Floor | 59.4022 | 15 | 6.7433
Total transmission load (KWh/day) |  |  | 40.8858
Internal Load |  |  | Air Infiltration Load |  |  | Equipment Load
People |  |  | Air changes per day | 6 |  | Fans
No. of people working inside per day | 2 |  | Volume of cold store (ft3) | 3292.4702 |  | No. of fans | 3
Hours of working per day | 6 |  | Total air change (cfm) | 13.7186 |  | Wattage of each fan | 185
Heat released by a person (W/hr) | 270 |  | HRV(cfm) | 62 | 1.2 | Hours of use per day | 16
People load (Kwh/day) | 3.24 |  | Power consumption (W) | 89 |  | Fan Load (KWh/day) | 8.88
|  |  | Running hour(h) HRV | 5.3104 |  | Total Equipment Load (KWh/day) | 8.88
Light |  |  | Enthalpy load(KWh/kg) | 0.012922
No. of lamps | 3 |  | Efficiency of HRV | 60
Wattage of each lamp | 35 |  | mass flow rate (kg/h) | 123.3254 | air density(kg/m3) | 1.184
Hours of use per day | 12 |  | heat load without HRV(Kw) | 1.5936
Lighting load (KWh/day) | 1.26 |  | Total heat load(KWh/day) | 3.3851
Total Internal Load (KWh/day) | 4.5
|  |  | Total Cooling Load (KWh/day) | 123.3237
|  |  | Safety Factor (%) | 10
|  |  | Final Cooling Load (KWh/day) | 135.6561
|  |  | Refrigeration system run hours per day | 16
|  |  | Refrigeration Cooling Capacity(KW) | 8.4785
|  |  | Refrigeration Cooling Capacity(Tons) | 2.4107
|  |  | Number of evaporators | 1
|  |  | Capacity of each evaporator (KW) | 8.4785
|  |  | Required Air throw (m) | 11.9616
Evaporators | Kw | Air throw(m)

## Sheet2
Chamber 2
General Specification |  |  |  |  | Condition | Temperature (oC) | Humidity (%)
Product | Potato |  |  |  | Ambient | 25 | 70
Sack Dimension (2a,2b,L) ( in cm) | 47 | 32 | 94 |  | Inside Storage | 4 | 90
Weight of potato per sack (kg) | 50
Volume of potato per sack (cm3) | 111036.4507
No. of sacks(single layer) | 58
Number of layers of sacks in each pallet | 6
No. of sacks | 348
Capacity of cold store (MT) | 17.4 |  |  |  |  | 31.7-
Volume of each pallet (m3) | 6.786
Room dimension (L,B,H) (in m) | 9.1186 | 5.5626 | 3.048
Total Volume of room (m3) | 154.6041
Store room dimension (L,B,H)(ft) | 23.401 | 15.9895 | 8.2
Storage Volume(ft3) | 3068.1964
Transmission Load
Wall | Polyurethane Insulation Panel
Product Load
U- Value (W/m2.K) (Wall 80mm) | 0.275 |  |  |  | Specific Heat Capacity of potato (KJ/Kg.oC) | 3.39
U- Value (W/m2.K) (Floor 50mm) | 0.43 |  |  |  | Respiration heat (KJ/Kg per day) | 3.6
[5 empty] | Mass of potato (kg) | 17400
[5 empty] | Time taken to cool the product (days) | 7
Surface | Area (m2) | Temperature (oC) | Cooling Load (KWh/day) |  | Product exchange load (KWh/day) | 49.155
North Wall | 27.7935 | 25 | 3.8522 |  | Product respiration load (KWh/day) | 17.4
West Wall | 16.9548 | 25 | 2.3499 |  | Total Product Load (KWh/day) | 66.555
East Wall | 16.9548 | 28 | 2.6856
South Wall | 27.7935 | 26 | 4.0356
Ceiling | 50.7231 | 20 | 5.3564
Floor | 50.7231 | 10 | 3.1408
Total transmission load (KWh/day) |  |  | 21.4205
Internal Load |  |  | Air Infiltration Load |  |  | Equipment Load
People |  |  | Air changes per day | 6 |  | Fans
No. of people working inside per day | 2 |  | Volume of cold store (ft3) | 3068.1964 |  | No. of fans | 3
Hours of working per day | 6 |  | Total air change (cfm) | 12.7842 |  | Wattage of each fan | 135
Heat released by a person (W/hr) | 270 |  | HRV(cfm) | 62 | 1.2 | Hours of use per day | 16
People load (Kwh/day) | 3.24 |  | Power consumption (W) | 89 |  | Fan Load (KWh/day) | 6.48
|  |  | Running hour(h) HRV | 4.9487 |  | Total Equipment Load (KWh/day) | 6.48
Light |  |  | Enthalpy load(KWh/kg) | 0.012922
No. of lamps | 2 |  | Efficiency of HRV | 60
Wattage of each lamp | 45 |  | mass flow rate (kg/h) | 123.3254 | air density(kg/m3) | 1.184
Hours of use per day | 12 |  | heat load without HRV(Kw) | 1.5936
Lighting load (KWh/day) | 1.08 |  | Total heat load(KWh/day) | 3.1545
Total Internal Load (KWh/day) | 4.32
|  |  | Total Cooling Load (KWh/day) | 101.93
|  |  | Safety Factor (%) | 10
|  |  | Final Cooling Load (KWh/day) | 112.123
|  |  | Refrigeration system run hours per day | 16
|  |  | Refrigeration Cooling Capacity(KW) | 7.0077
|  |  | Refrigeration Cooling Capacity(Tons) | 1.9925
|  |  | Number of evaporators | 1
|  |  | Capacity of each evaporator (KW) | 7.0077
|  |  | Required Air throw (m) | 7.1345
Evaporators | Kw | Air throw(m)
CR-E335N 078Z | 7.8 | 7.3

## Sheet3
Project Name: Cold Store Installation
Location: Lele (27.5753120, 85.3505281)
Date: 2/18/2024
Client: Kishan Kendra
Item | Description | Qty. | Unit | Rate | Total
Room Insulation
Polyurethane prefabricated sandwiched panels with pressure injected polyurethane foam insulation of density 42 kg/cu. M and cladded with 0.5mm thick white Lacquered galvanised steel sheet 1122 SM panels as room insulation complete with aluminium supports.The panels should be suplied with all accessories to support all the four walls and roof in an open space
Wall Panel-80mm
| 1000mm wide 8.5 ft long*46 | 1282.48 | sq.ft
Corner Panel-80mm thick
| 300mm/300mm 8.5ft long*6 | 51 | ft |  |  | Detail Estimate of Cold Store Item
Project Name: kishan kendra cold store
| Ceiling Panel ( Self Suppoting )-80mm |  |  |  |  | Site: Lele, Lalitpur
| 1200mm wide 39.75 ft long*3 | 469.4872 | sq.ft |  |  | A. COLD ROOM PANELS & ACCESSORIES:
| 1200mm wide 23.91 ft long*4 | 376.5347 | sq.ft |  |  | S.N. | DESCRIPTION
[8 empty] | QTY | UNIT | UNIT RATE | AMOUNT
| Floor insulation-50mm | [5 empty] | COLD ROOM PANELS & ACCESSORIES:
| 1000mm wide 44.75 ft long*4 | 586.9888 | sq.ft |  |  | Modular Wall Panels / Ceiling Panels :
| 1000mm wide 28.67 ft long*5 | 470.188 | sq.ft |  |  | 1 | Supply, installation, transportation, testing and commissioning of 80mm Polyurethane prefabricated sandwiched panels with pressure injected polyurethane foam insulation of density 42 kg/cu. M and cladded with 0.5mm thick white Lacquered galvanised steel sheet 1122 SM panels as room insulation complete with aluminium supports.The panels should be suplied with all accessories to support all the four walls and roof in an open space Single Piece of any suitable size 1.0/1.1 m width x 3.76 m length for wall panels single length and 1.0m x 4 m | 120 | Sq.M
| Tar felt sheet-3mm | 1057.1768 | sq.ft |  |  | 2 | Supply of 50mm Thick PUF Slab, PUF density 40kg±2/m3. For Cold room along with Floor insulation material (bitumen and 2 layer of 2.5 mm thick Tar Felt sheet wo layer of bitumin of 1.5 kg / sq.m. | 55 | Sq.M
| Plastic sheet | 1057.1768 | sq.ft |  |  | 3 | Supply of 80mm Thick PUF " L" corner300 mm width from outer side, inner side 0.5mm and 0.5mm outer RAL 9002 PPGI sheet, PUF density 40kg±2/m3. single length (without joint). Joint tounge and groove clading with cam lock and complete cealing material or silicon glue. | 17 | RM
[6 empty] | 4 | Supply of sliding door, 80mm Thick PUF Insulation,0.6mm poweder coated Finish (For Positive temperature +1degree) (Density 45kg/m3) wall fixing frame with Door Opener & Closure, Pad Lock, door sliding mechanism, Door Size - (opening width min 900 mm, Height min 2000mm), | 2 | Nos.
| Cold Room Door |  |  |  |  | 5 | Supply and installation of material (Flushing, Silicon, Pop Revit's, for partition joints for panels in corner. (wall to wall corner as well as ceiling to wall joint. Joining detail to be provided by PUF panel manufacturer with cost including. |  | Rm
| Cold room doors whose overall size is 2130mm high by 900mm wide complete withopening handles and made of 80mm TSSC sandwich panels and cladded micron plasstisol coated G.I sheet with fittings and 2 No. gasket TPE rubber, slab gaskets even internally | 2 | No. |  |  | 6 | U channel and fixing accessories 0.5 mm sheet width 105 mm and height 40 mm ( Screw fastner with rawl plug pop rivets ) Joining detail to be provided by PUF panel manufacturer with cost including. | 40 | Rm
[9 empty] | Total cost for panel |  | -
Lighting
| Led ceiling lighting, programmable through the control Panel. |  |  |  |  | B. Air Cooled Scroll/ Receprocating Refrigeration Unit
| 45W | 2 | No. |  |  | SR.NO.
| 35W | 3 | No. |  |  |  | DESCRIPTION | QTY | UNIT | UNIT RATE | AMOUNT
Air Cooled Scroll/Receprocating Refrigeration Unit
| Evaporator Unit |  |  |  |  | 7 | Supply, Installtion, Testing & Commissioning of Condensing unit and cooling unit Condensing unit include Scroll hermetic compressor, air cooled condenser with condenser fan, liquid accumulator, oil separator, liquid receiver, integrated HP/LP/OLR and Drives, eco-friendly refrigerant R404A/134a controls gauges, Starter, control Panel, anti-vibration pads etc. Compressors Motor shall be suitable for 415±10% 50 cycles. 3 phase AC supply and motor cable terminal box shall be suitable to connect Copper Cabling. Cooling unit include cooling coil, two evaporator fan, Thermostatic expansion valve, Solenoid coil, Thermostat, Electrical Defrost heater, Drain pan, drain pipe, electrical terminal box with water shield. fan motor shall be 220/1phase/50 Hz cost involve with foundation work with metalic frame.
| The evaporator unit with a cooling load of 7.8 Kw with through of 7.3m complete with cooling coil, defrost heater, expansion valve, air circulating fans, guards, drip tray, drainage pipework outlet, supports, etc. The unit to be complete with a power supply. including | [5 empty] | Design Ambient:30°C& 70%RH,
Inside temp: 4°C,
| Evaporator Unit Support | [5 empty] | SST: -3.05±1°C
| Allow for a suitable wall mounting support for the above that can match the panel used for constructing the cold room. | [5 empty] | Capacities: kW output at design condition.
[6 empty] | 8 | Heat Load min. 9 kW output at design condition. Compressor power: approx.5.5 kW Single compressor 440±10%/3ph/50Hz Condenser fan: 1 ph Singlefan220±/1ph/50Hz10% Number of condenser fan 2 Electric Power: = approx.500 W Air cooled condenser consisting of coppertube with hydrophilic coated aluminum Fins Evaporator capacity: 8.5kW Evaporator Fan:1 PH 220V/50 Hz Number of evaporator fan : 2nos. Evaporator Fan power approx. 0.33 HP Air through 12 m | 2 | Set
| Condensing Unit |  |  |  |  | 9 | Heat Load min. 8 kW output at design condition. Compressor power: approx.5.5 kW Single compressor 440±10%/3ph/50Hz Condenser fan: 1 ph Singlefan220±/1ph/50Hz10% Number of condenser fan 2 Electric Power: = approx.500 W Air cooled condenser consisting of coppertube with hydrophilic coated aluminum Fins Evaporator capacity: 7 kW Evaporator Fan:1 PH 220V/50 Hz Number of evaporator fan : 2nos. Evaporator Fan power approx. 0.33 HP Air through 7 m | 2 | Set
| A 7.8Kw air cooled condensing unit with semi-hermetic reciprocating compressor capable of a cooling load to match the evaporator unit's defrosting and to be complete with fan, compressor, condenser, liquid receiver, controls, anti-vibration mountings etc. |  |  |  |  | 10 | Supply installation testing and commissioning of PLC base indoor temperature, humidity, defrost control with difrost timer unit | 2 | set
[6 empty] | 11 | Supply installation of Condensate water drain pipe with necessary accessories |  | Rm
| Control Panel |  |  |  |  | 12 | Supply, Installtion, Testing & Commissioning of Aultrasonic Humidifier with all control accessories for humidity control for humidification(min 30 Ltr/24 hr) | 2 | Nos.
| The panel shall be complete with contactors, timers and all other accessories necessary for the automatic operation of the cold store. |  |  |  |  | 13 | Supply, Installtion, Testing & Commissioning ofHeat recovery Ventilation units (HRVs) for Long storage room. Capacity: 100CFM | 2 | Nos.
[6 empty] | 14 | Supply of Refrigerant R404a/R134a for complete units each Cylinder with 11.5kg net weight or as required by condensers provided. | 1 | cylinder @13.6 kg
| REFRIGERANT GAS : Supply and Charging of R-404A refrigerant gas | 11kg |  |  |  | 15 | 4Ft Low Noise level type Centrifugal Air curtain over the main Cold room entrance door including control system for operation only door open time. | 2 | Nos.
A | [5 empty] | C. Electrical Accessories
| DRAIN PIPING : Supply, Installation and Testing of Hard PVC drain piping insulated out of nitrile rubber material of approved make as per specification complete with supports, consumables, fittings, pipe sleeves, U trap, leak arresting of following sizes. |  |  |  |  | SR.NO.
[7 empty] | DESCRIPTION | QTY | UNIT | UNIT RATE | AMOUNT
B | CONTROLLER AND DISPLAY SYSTEM : The unit is fitted with a micro-processor based digital electronic temperature controller cum indicator for easy readability along with audio-visual alarm system. The controller should have the facility to set temperature and humidity value and also the safety limits for temperature and humidity. The temperature control to be within +/- 10C at the sensing point. An audible alarm should be provided in the event of actual values exceeding the set limits, connected to the main building and security guard room. In the event of failure of the main mechanical refrigeration system or dehumidification device, the switch over to standby system should be automatic with indication of failure of main system.In the event of power failure,module should have delayed start in a sequesnce so that power lines are not loaded. | hum +-5, tem +-1 |  |  |  | Electrical Accessories
[6 empty] | 16 | Supply, installation, transportation, testing of Power Socket including wiring, 16amp 3*3 power socket inside coldroom | 4 | Nos.
[6 empty] | 17 | Supply, installation, transportation, testing of Light including switch and wiring LED round panel light of 35W inside chamer 1 | 3 | Nos.
[6 empty] | 18 | Supply, installation, transportation, testing of Light including switch and wiring LED round panel light of 45W inside chamer 2 | 2 | Nos.
C | [5 empty] | 19 | Supply, installation, transportation, testing of circuit breaker with wall mount box. 32amp MCB for 4 condenser unit including suitale gauge wire, 16amp MCB for 2 chamber for power socket and lighting inside coldroom | 6 | Nos.
[9 empty] | Total Machine cost |  | -
[7 empty] | Total amount without VAT |  |  |  | -
[7 empty] | Total amount with VAT |  |  |  | -