## Calculation-F
Hydraulic calculation for Sprinkler System Design
NFPA 13
Hazard classification : |  | Ordinary hazard group 1
Ordinary Hazard Group 1
Area coverage by sprinkler (As): |  |  | 130 | ft² | As per NFPA-13 |  |  |  | Automobile parking
Bakeries
Beverage manufacturing
Density(D) : | 0.15 | gpm/ft² |  |  | As per NFPA-13 |  |  |  | Canneries
Dairy products
Total area protection(Ap) : |  | 1168.02 | ft² |  | As per NFPA-13 |  |  |  | Electronic plants
glass products manufacturing
K factor | = | 5.6 |  |  | As per NFPA-13 |  |  |  | Laundries
Restaurant service areas
Total number of sprinkler = |  | Ap/As | [6 empty] | showrooms
| N | = | 8.9848
| Suppose (N) | = | 9 | Sprinklers
Remote Area Length = |  |  | 41.0116 | ft | 1.2 (Ap)2 | As per NFPA-13
Remote Area Width = |  |  | 28.4803 | ft
Distance between sprinklers (S) = |  |  | 15 | ft | Max distance is 15ft as per NFPA-13, Ordinary hazard
Distance between branch lines (L) = |  |  | 8.6667 | ft | As/S
Branch number of sprinklers = |  |  | 2.7341 |  | 1.2 (Ap)2/S
| Suppose | = | 3
Flow rate per sprinkler(Qs)= D * As
| Qs | = | 19.5 | gpm
| Qs =k * p½ |  | P residual =(Qs/k)2
| P residual | = | 12.1253 | psi | As per NFPA min. residual pressure 20psi for Ordinary Hazard
Start Point | P1 residual | = | 20 | psi | We will take this value, if take public water supply pipeline
Material of pipe black steel schedule 40
| c | = | 120
| path | Q(gpm) | D(in) | Pipe | Fitting and | N | Equivalence | Length(ft) | Friction loss | pressure | P(psi) | Notes
|  |  |  | Length(ft) | Devices |  | Length (ft) | Total | (Psi/ft) | friction(Psi)
| 1-a | 19.5 | 1 | 13.17 | 90° standard elbow | 2 | 2 | 22.17 | 0.15675 | 3.4752 | 23.4752 | P1 | 23.4752 | P(friction)=total length*friction loss per feet
[5 empty] | Tee or Cross 90° | 1 | 5 |  |  |  |  | k = | 5.6 | P=Presidual+Pfriction
[5 empty] | NONE |  | 0 |  |  |  |  | Q2 = | 27.1327 | Q2=K(P)^1/2
| 2-a | 19.5 | 1 | 8.417 | Tee or Cross 90° | 1 | 5 | 15.417 | 0.15675 | 2.4167 | 22.4167 | P2 | 22.4167
[5 empty] | 90° standard elbow | 1 | 2 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q3 = | 26.5139
| a-b | 53.6466 | 1 | 2.759 | Tee or Cross 90° | 1 | 5 | 7.759 | 1.0193 | 7.9088 | 53.8007
NONE
[5 empty] | NONE |  | 0
| 3-b | 19.5 | 1 | 9.022 | 90° standard elbow | 1 | 2 | 16.022 | 0.15675 | 2.5115 | 22.5115 | P3 | 22.5115
[5 empty] | Tee or Cross 90° | 1 | 5 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q5 = | 26.5699
.
| b-c | 80.2165 | 1.25 | 6.464 | Tee or Cross 90° | 1 | 6 | 12.464 | 0.72375 | 9.0208 | 76.3122
[5 empty] | NONE |  | 0
[5 empty] | NONE |  | 0
C62 | 4-c | 19.5 | 1 | 3.802 | Tee or Cross 90° | 1 | 5 | 10.802 | 0.15675 | 1.6933 | 21.6933 | P6 = | 21.6933
[5 empty] | 90° standard elbow | 1 | 2 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q6 = | 26.0826 | Q (Adjust)=QLx√P/P
| c-d | 106.2991 | 1.5 | 14.933 | Tee or Cross 90° | 1 | 8 | 22.933 | 0.50138 | 11.4982 | 98.0055
[5 empty] | NONE |  | 0
[5 empty] | NONE |  | 0
| 5-d | 19.5 | 1 | 3.517 | Tee or Cross 90° | 1 | 5 | 10.517 | 0.15675 | 1.6486 | 21.6486 | P8 = | 21.6486
[5 empty] | 90° standard elbow | 1 | 2 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q8 = | 26.0557
| d-e | 132.3548 | 1.5 | 1.26 | Tee or Cross 90° | 1 | 8 | 9.26 | 0.75215 | 6.9649 | 119.654
[5 empty] | NONE |  | 0
[5 empty] | NONE |  | 0
| 7-8. | 19.5 | 1 | 9.97 | 90° standard elbow | 2 | 5 | 19.97 | 0.15675 | 3.1304 | 23.1304 | P11 = | 23.1304
[5 empty] | NONE |  | 0 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q11 = | 26.9327
| f-7 | 46.4327 | 1 | 8.94 | 90° standard elbow | 1 | 2 | 15.94 | 0.78033 | 12.4384 | 35.5688 | P10 = | 35.5688
[5 empty] | Tee or Cross 90° | 1 | 5 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q10 = | 33.3982
| 6-f | 19.5 | 1 | 9.961 | Tee or Cross 90° | 1 | 10 | 21.961 | 0.15675 | 3.4425 | 23.4425 | P10 = | 23.4425
[5 empty] | 90° standard elbow | 1 | 2 |  |  |  |  | k = | 5.6
[5 empty] | NONE |  | 0 |  |  |  |  | Q10 = | 27.1138
| e-g | 106.9446 | 2 | 6.686 | Tee or Cross 90° | 1 | 10 | 16.686 | 0.12491 | 2.0842 | 61.0954
[5 empty] | NONE |  | 0
[5 empty] | NONE |  | 0 | [6 empty] | Q (Adjust)=QLx√P/P
| g-h | 239.2994 | 2 | 6.686 | 90° standard elbow | 1 | 5 | 11.686 | 0.55422 | 6.4766 | 187.226
[5 empty] | NONE |  | 0
[5 empty] | NONE |  | 0
| h-i | 239.2994 | 6 | 48 | Butterfly valve | 0 | 6 | 48 | 0.0026309 | 0.12628 | 187.3523
[5 empty] | NONE |  | 0
[5 empty] | NONE |  | 0
| i-j | 239.2994 | 6 | 16.4 | Butterfly valve | 1 | 10 | 160.4 | 0.0026309 | 0.42199 | 187.7743
[5 empty] | 90° standard elbow | 1 | 14
[5 empty] | Tee or Cross 90° | 4 | 30
Total length | 169.987
Total pressure (friction+ residual) |  | 187.7743
GPM | 239.2994
P (friction and residual) |  | = | 12.9466 | bar | 0.0689 x 187.77 |  |  | Note: | 1 foot WC= | 0.03bar
[9 empty] | 1 foot WC= | 0.434psi
P (static) |  | = | 5.0996 | bar | 169.987feet x 0.03 |  |  |  | 1 psi = | 0.0689bar
[9 empty] | 1 bar = | 14.5psi
P (total) |  | = | 18.0462 | bar | 14.6 x 14.5
PUMP HEAD PRESSURE = 18.05 BAR
PUMP FLOW CAPACITY = 239.30 GPM

## Tables
Classification of Occupancies.
| Light Hazard Occupancies. | Ordinary Hazard Occupancies |  | Extra Hazard Occupancies
|  | Group 1 | Group 2 | Group 1 | Group 2
| Churches | Automobile parking | Cereal mills | Aircraft hangars | Asphalt saturating
| Clubs | Bakeries | Chemical plants — ordinary | Combustible hydraulic fluid use areas | Flammable liquids spraying
| Eaves and overhangs, | Beverage manufacturing | Confectionery products | Die casting | Flow coating
| Educational | Canneries | Distilleries | Metal extruding | Manufactured home
| Hospitals | Dairy products | Dry cleaners | Plywood and particles | Open oil quenching
| Institutional | Electronic plants | Feed mills | Printing | Plastics processing
| Libraries, | glass products manufacturing | Horse stables | Rubber | Solvent cleaning
| Museums | Laundries | Leather goods manufacturing | Saw mills | Varnish and paint dipping
| Nursing or accomodation | Restaurant service areas | Libraries — large stack room areas | Textile All kind
| Offices, | showrooms | Machine shops | Upholstering with plastic foams
| Residential |  | Metal working
| Restaurant seating areas |  | Mercantile
| Theaters and auditoriums, |  | Paper and pulp mills
| Unused attics |  | Paper process plants
Piers and wharves
Post offices
Printing and publishing
Repair garages
Resin application area
Stages
Textile manufacturing
Tire manufacturing
Tobacco products manufacturing
Wood machining
Wood product assembly
Table 14.5.2.2.1 Light Hazard Pipe Schedules
| Steel |  | Copper
| 1 in. | 2 sprinklers | 1 in. | 2 sprinklers
| 1¼ in. | 3 sprinklers | 1¼ in. | 3 sprinklers
| 1½ in. | 5 sprinklers | 1½ in. | 5 sprinklers
| 2 in. | 10 sprinklers | 2 in. | 12 sprinklers
| 2½ in. | 30 sprinklers | 2½ in. | 40 sprinklers
| 3 in. | 60 sprinklers | 3 in. | 65 sprinklers
| 3½ in. | 100 sprinklers | 3½ in. | 115 sprinklers
| 4 in. | See Section 8.2 | 4 in. | See Section 8.2
Table 14.5.2.4 Number of Sprinklers Above and Below a Ceiling
| Steel |  | Copper
| 1 in. | 2 sprinklers | 1 in. | 2 sprinklers
| 1¼ in. | 4 sprinklers | 1¼ in. | 4 sprinklers
| 1½ in. | 7 sprinklers | 1½ in. | 7 sprinklers
| 2 in. | 15 sprinklers | 2 in. | 18 sprinklers
| 2½ in. | 50 sprinklers | 2½ in. | 65 sprinklers
Table 14.5.3.4 Ordinary Hazard Pipe Schedule
| Steel |  | Copper
25 | 1 in. | 2 sprinklers | 1 in. | 2 sprinklers
32 | 1¼ in. | 3 sprinklers | 1¼ in. | 3 sprinklers
40 | 1½ in. | 5 sprinklers | 1½ in. | 5 sprinklers
50 | 2 in. | 10 sprinklers | 2 in. | 12 sprinklers
65 | 2½ in.. | 20 sprinklers | 2½ in. | 25 sprinklers
80 | 3 in. | 40 sprinklers | 3 in. | 45 sprinklers
| 3½ in. | 65 sprinklers | 3½ in. | 75 sprinklers
| 4 in. | 100 sprinklers | 4 in. | 115 sprinklers
| 5 in. | 160 sprinklers | 5 in. | 180 sprinklers
| 6 in. | 275 sprinklers | 6 in. | 300 sprinklers
| 8 in. | See Section 8.2 | 8 in. | See Section 8.2
Table 14.5.3.5 Number of Sprinklers — Greater than 12-ft (3.7-m) Separations
| Steel |  | Copper
| 2½ in. | 15 sprinklers | 2½ in. | 20 sprinklers
| 3 in. | 30 sprinklers | 3 in. | 35 sprinklers
| 3½ in. | 60 sprinklers | 3½ in. | 65 sprinklers
Table 14.5.3.7 Number of Sprinklers Above and Below a Ceiling
| Steel |  | Copper
| 1 in. | 2 sprinklers | 1 in. | 2 sprinklers
| 1¼ in. | 4 sprinklers | 1¼ in. | 4 sprinklers
| 1½ in. | 7 sprinklers | 1½ in. | 7 sprinklers
| 2 in. | 15 sprinklers | 2 in. | 18 sprinklers
| 2½ in. | 30 sprinklers | 2½ in. | 40 sprinklers
| 3 in. | 60 sprinklers | 3 in. | 65 sprinklers
Table 10.10.2.1.3 Flow Required to Produce a Velocity of 10 ft/sec (3 m/sec) in Pipes
| PIPE SIZE |  | FLOW RATE
| IN | mm | gpm | L\S
| 4 | 102 | 390 | 1476
| 6 | 152 | 880 | 3331
| 8 | 203 | 1560 | 5905
| 10 | 254 | 2440 | 9235
| 12 | 305 | 3520 | 13323

## Hazen Williams Equation
Hazen-Williams Equation for Pressure Loss in Pipes
Specified Data
l = length of pipe (ft) | 11
c = Hazen-Williams roughness constant | 120
q = volume flow (gal/min) | 206
dh = inside or hydraulic diameter (inches) | 2
Calculated Pressure Loss
f = friction head loss in feet of water per 100 feet of pipe (ft H20 per 100 ft pipe) | 98.3255
f = friction head loss in psi of water per 100 feet of pipe (psi per 100 ft pipe) | 42.28
Head loss (ft H20) | 10.8158
Head loss or Friction loss (psi/ft) | 4.6508
Calculated Flow Velocity
v = flow velocity (ft/s) | 21.0485